## IEEE Data 10yr
OUTAGE DATA SUMMARY
Cause | 1993 | 1994 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 6 Yr. Ave.
Overload | 0 | 2 | 1 | 2 | 0 | 1 | 0 | 2 | 3 | 0 | 0 | 0 | 0.83333
Comp. Failure | 70 | 51 | 80 | 71 | 79 | 71 | 70 | 62 | 84 | 75 | 59 | 67 | 69.5
Operator Error | 1 | 1 | 5 | 5 | 9 | 9 | 17 | 12 | 19 | 9 | 17 | 9 | 13.8333
ML&P loss of Gen. | 0 | 2 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 0 | 0 | 0.83333
Protective Relay Misoper. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 1 | 2 | 0.83333
Storm or Wind | 28 | 14 | 1 | 15 | 1 | 29 | 3 | 4 | 3 | 7 | 18 | 4 | 6.5
Fire | 0 | 2 | 2 | 5 | 1 | 0 | 0 | 2 | 3 | 5 | 1 | 1 | 2
Vehicle | 16 | 11 | 13 | 5 | 12 | 11 | 5 | 6 | 14 | 15 | 13 | 12 | 10.8333
Dig-In | 11 | 9 | 20 | 13 | 10 | 17 | 14 | 10 | 10 | 12 | 6 | 4 | 9.3333
Inadverent Contact | 19 | 28 | 30 | 34 | 50 | 42 | 49 | 49 | 50 | 43 | 30 | 16 | 39.5
Vandalism | 0 | 0 | 4 | 3 | 1 | 3 | 0 | 1 | 0 | 0 | 1 | 0 | 0.33333
Other | 3 | 2 | 20 | 29 | 28 | 28 | 25 | 10 | 19 | 25 | 21 | 26 | 21
Other Loss of Gen. | 6 | 3 | 1 | 5 | 2 | 2 | 8 | 2 | 3 | 3 | 3 | 0 | 3.1667
Customers Equipment | 1 | 1 | 6 | 2 | 1 | 2 | 5 | 2 | 5 | 3 | 4 | 3 | 3.6667
Total | 155 | 126 | 184 | 189 | 195 | 216 | 197 | 164 | 215 | 199 | 174 | 144 | 182.1667
Continuity by Customer Hrs | 0.99988 | 0.99993 | 0.99989 | 0.9999 | 0.99988 | 0.99966 | 0.99991 | 0.99991 | 0.99991 | 0.99991 | 0.99994 | 0.99989 | 0.99991
Continuity by Megawatt Hrs. | 0.99991 | 0.99993 | 0.99984 | 0.9998 | 0.99986 | 0.99949 | 0.99986 | 0.99991 | 0.99984 | 0.99983 | 0.99991 | 0.99988 | 0.99987
CAIDI | 0.51712 | 0.36773 | 0.86892 | 0.93061 | 1.095 | 1.1162 | 0.42769 | 0.56167 | 0.79468 | 0.80249 | 0.97771 | 1.3426 | 0.8178
SAIDI | 1.0457 | 0.59644 | 0.99024 | 0.85511 | 1.0606 | 2.9573 | 0.82782 | 0.75638 | 0.77503 | 0.8213 | 0.53986 | 0.96176 | 0.78036
SAIFI | 2.0222 | 1.622 | 1.1396 | 0.91886 | 0.9686 | 2.6495 | 1.9356 | 1.3467 | 0.97528 | 1.0234 | 0.55217 | 0.71635 | 1.0916
Ave. # of customers outaged | 381.6 | 379 | 180.7 | 142.4 | 147.1 | 363.6 | 291.7 | 243.8 | 135 | 153.6 | 95.5 | 149.7 | 178.2167
Total customers hrs lost | 30585.7 | 17559.87 | 28887.32 | 25040.05 | 31412.18 | 87658 | 24575.38 | 22458.55 | 23071 | 24533.78 | 16248 | 28937 | 23303.9517
Total Mwh lost | 71.6 | 59.4 | 135.7 | 179.8 | 125.5 | 456.8 | 128.9 | 80.2 | 145.2 | 168.8 | 93.1 | 139.1779 | 125.8963
DEFINITIONS |  |  | Benchmarks are derived from APPA 2003 Distribution System Reliability & Operations Survey
Pages 14-15 for public utilities with 20,000 to 40,000 customer meters
CAIDI: |  |  | Defined as the average length of an interruption, weighted by the number of customers
affected, for customers interrupted during a specific time period. Benchmark is 1.3 hours.
SAIDI: |  |  | Defined as the average interruption duration for customers served during a specified time
period. Benchmark is .86 hours.
SAIFI: |  |  | Defined as the average number of times that a customer is interrupted during a specified
time period. Benchmark is 2.52 Interruptions per customer
ORIGIN: See email 10/23/07

## 79 thru 84
OUTAGE DATA SUMMARY
Cause | 1979 | 1980 | 1981 | 1982 | 1983 | 1984 | 6 Yr Ave.
Overload | 6 | 19 | 2 | 3 | 10 | 5 | 7.5
Comp. Failure | 38 | 39 | 23 | 43 | 37 | 32 | 35.3333
Operator Error | 2 | 2 | 3 | 0 | 5 | 9 | 3.5
ML&P loss of Gen. | 11 | 17 | 4 | 2 | 4 | 3 | 6.8333
Protective Relay Misoper. | 0 | 1 | 0 | 0 | 0 | 1 | 0.33333
Storm or Wind | 14 | 11 | 1 | 9 | 2 | 3 | 6.6667
Fire | 0 | 0 | 0 | 0 | 0 | 1 | 0.16667
Vehicle | 15 | 10 | 7 | 11 | 15 | 13 | 11.8333
Dig-In | 13 | 14 | 15 | 24 | 45 | 37 | 24.6667
Inadverent Contact | 0 | 0 | 0 | 1 | 7 | 11 | 3.1667
Vandalism | 0 | 0 | 1 | 1 | 2 | 0 | 0.66667
Other | 16 | 17 | 15 | 16 | 8 | 12 | 14
Other Loss of Gen. | 0 | 1 | 1 | 2 | 1 | 4 | 1.5
Customers Equipment | 4 | 1 | 0 | 0 | 1 | 0 | 1
Total | 119 | 132 | 72 | 112 | 137 | 131 | 117.1667
Continuity by Customer Hrs | 0.99921 | 0.99857 | 0.9997 | 0.99935 | 0.99973 | 0.99939 | 0.99933
Continuity by Megawatt Hrs. | 0.99917 | 0.99839 | 0.99973 | 0.99937 | 0.99984 | 0.99938 | 0.99931
CAIDI | 1.0352 | 0.99409 | 0.96161 | 1.4533 | 0.91363 | 1.7742 | 1.1887
SAIDI | 6.9194 | 12.5718 | 2.5916 | 5.6634 | 2.3351 | 5.3666 | 5.908
SAIFI | 6.6844 | 12.6465 | 2.6951 | 3.8968 | 2.5559 | 3.0248 | 5.2506
Ave. # of customers outaged | 945.3 | 1700.2 | 621.6 | 604.4 | 342.5 | 487.4 | 783.5667
Total customers hrs lost | 116439.58 | 218032.43 | 43036.7 | 98378.65 | 42865.9 | 113283.98 | 105339.54
Total Mwh lost | 392.2147 | 797.6371 | 131.1717 | 367.54 | 92.8167 | 407.7874 | 364.8613